OWNER’S MANUAL

FOR

INSTA-POWERTM

## TRANSFORMERS

COMFORT INSTA- POWER LTD. Works: Plot no. 275-276, GIDC Estate, Anjar- Kutch- Gujarat -India. Telephone: 02836- 325565 Telefax 02836- 242776 Email info@comfortinstapower.com

1. 	TRANSPORT & HANDLING :

1.1 	General :

All our Transformers are designed, manufactured and tested with due care. Routine Tests in accordance with I.S. 2026/I.S. 1180 are carried out on all transformers. They will give long & trouble free service when properly installed, operated & maintained. In case anything abnormal occurs during the service, reference should be made to us giving complete particulars as to the nature and the extent of abnormality together with the name-plate particulars in order to assist identification of the transformer. As efforts are being constantly made to improve designs and services, the transformers supplied may differ in minor details from the data given here under. Any additional information, if required, can be supplied on request.

  - Transport :

Transformers of rating 1250KVA and above are generally dispatched with their external fittings dismantled to the extent required and weather-proof blanking plates are provided wherever necessary prior to dispatch. External arrangement drawings indicate various accessories, dismantled for transport, with asterisks against list of fittings with an appropriate note.

All parts which are dismantled are packed either separately or in a group as appropriate. Each packing case is marked  or numbered and is included in the packing list along with the description of contents.

Transformers are dispatched in one of the following modes :

- Completely filled with oil.

- With oil covering coils and top yoke (approx. 40mm below top cover). Oil for topping up, filling in radiators etc. is dispatched separately in sealed drums. Space above oil level is filled with air at normal atmospheric pressure.

Accessories such as  conservator, radiators, oil filled bushings etc., which are dispatched in different packages, are given numbers and these numbers are indicated together with contents, in the packing list.

  - Unloading & Handling:

On receipt at site, transformers should be unloaded by means of crane or lifting devices of adequate capacity. All lifting lugs must be used to avoid unbalanced lifting and undue stresses on lugs. Lifting lugs provided for partial lifting (e.g. for active part, conservator etc. ) must not be used for lifting complete transformer. Parts other than lifting lugs must not be used for lifting. While slinging care should be taken to avoid slings touching other parts.

All other parts & case containing accessories should be unloaded by using lifting lugs. They should be handled in their upright position as indicated on the cases.

Transformers should be carefully examined for transit damages. External damages could be indicative of severe internal damages. Following should be particularly observed :

Transformers should be carefully examined for transit damages. External damages could be indicative of severe internal damages. Following should be particularly observed :

- Dents on tank wall

- Damage to protruding parts like valves, sight glass etc.

- Oil leakage around or through welds.

Packed components should be carefully unpacked and all parts/components received should be examined for transit damages.

Rollers should be used for shifting the transformer from one place to other. Roller axles or radiators should not be slinged for the purpose of towing. Pulling holes provided on the tank for this purpose should only be used.

Transformers of higher ratings are provided with four jacking pads. Each jacking pad is designed to take approximately 25% of the total load. Under no circumstances, jacks should be used anywhere else other than these specially provided pads.

  - Storage:

On receipt of the Transformer at site, it is desirable to install and commission the transformer with minimum delay. In case, this is not possible, the silica-gel breather should be fitted. The breather incorporates an oil sealing device which must be filled with oil to the marked level to be effective.  A periodic watch should be kept on the silica-gel breather to ensure that the gel is blue. The gel should be replaced or dehydrated immediately on it turnings pink.

  - It is advisable to check the condition of silica gel during storage atleast once a week and Break Down Voltage (BDV) of oil atleast once in a month and should be maintained at a level of  50KV. It is desirable to keep the transformer energized even at a low voltage so that the oil temperature is about 100 to 150 C higher than the surrounding ambient temperature.

  - Even during temporary  storage, it is recommended to mount rollers by jacking-up the transformers to enable free flow of air underneath.

  - The tap changer should be operated at six monthly intervals. Two or three runs from one end of the range to the other are considered sufficient.

  - Accessories like bushings, buchholz relay, dial type temperature indicator, terminal box, radiators, all pipe work, should be stored indoors till such time they are not required. If they are not stored properly, they are likely to be damaged. The conservator pipe work and radiators are dispatched with blanking plates and these are to be stored with their blanking plates, in position.

If these are stored for a longer period like six months or so, it is advisable to flush them with clean transformer oil before use.

2.		FITTINGS & ACCESSORIES :

  - Rating & Terminal marking plate : ( R& D Plate)

The transformers is supplied with rating and terminal marking plate made out of non-corrosive metal. The plate contains information concerning the rating, voltage ratio, weights, oil quantity, vector group, etc. The plate also includes unit Sr. No. and year of manufacturing.

  - Tap changing arrangement:

    - Off circuit switch: The transformer is normally fitted with an off circuit tap changing switch to obtain required voltage ratio. It can be hand-operated by a switch handle mounted either on tank cover or on the tank side.  The locking device is fitted to the handle to lock in any tap position. The switch mechanism is such that it can be locked only when it is located in its proper position and not in any intermediate position.

  - Earthing Terminals:

The core laminations assembly is connected to core clamping frame which is in turn connected to the tank. Two earthing terminals are provided on the transformer tank. The earthing terminals should be connected to the earthing.

  - Lifting Lugs:

Two/Four lifting lugs of adequate capacity are provided on tank sides/ top cover to lift fully assembled transformer filled with oil.

All lugs are designed for simultaneous use and must be used accordingly. Two/Four lifting lugs are provided for untanking the core and windings of larger capacity transformers.

All heavy fittings are also provided with individuals lifting lugs.

  - Valves:

Every transformer is provided with drain cum filter valve at bottom of the tank, and filter valve at top of the tank. Valves are fitted with plugs/ blanking plates to stop oil coming out.

Mainly two types of valves are provided.

- Wheel Valves

- Butterfly Valves.

The Wheel valves are used either with female screw threads or with flanges. These are of gun-metal / cast iron type.

Generally, one isolating valve also known as shut off valve is provided for transformer upto 2000 KVA between conservator and buchholz relay.

The Butterfly type Cast steel valves with the machined flanges are used at points of connection between tank and detachable radiators.

  - Buchholz Relay :

Buchholz Relay is a very sensitive, gas and oil operated apparatus which detects formation of gas or development of sudden pressure inside the oil filled transformer. It is connected to protection circuits to give an early audible alarm of gas collection and to disconnect the transformer from supply in case of severe fault inside the transformer.

The basic function of the relay is to initiate an electrical signal in the protection circuit when:

- Gas is a accumulated in the relay, as result of incipient level.

- Surge of oil is developed on account of sudden increase in pressure inside the transformer due to severe fault.

- Oil level in the relay is reduced below the minimum level.

Buchholz relay operates in the following manner :

The relay comprises a housing containing two pivoted buckets/ Floats counter balanced by dead weights. Each bucket assembly carries a mercury switch. The relay is fitted in the oil connection between conservator and tank.

Due to gas collection, the oil level inside the relay drops and the upper bucket moves down. This tilts the mercury switch bringing fluid mercury in such a position that it bridge the normally open (NO) contacts. Other probable reasons for dropping of oil level in the relay are :

- Leakage of oil from main tank, conservator or relay itself.

- Collection of air in the relay which is trapped earlier in the tank and in the winding.

The lower bucket operates similar to upper bucket when level in the relay drops further. However, important function of this relay is to disconnect transformer from circuit under sudden development of pressure inside the transformer due to severe internal fault. In such cases, gas generation is rapid and displaced oil surges through the relay impinging on the baffle plates causing lower bucket to tilt and close the Normally open (NO)contact of the mercury switch carried by it.

Upper bucket contacts (A) are connected to audible alarm-‘A’-circuit and lower bucket contacts-(T)-are connected to trip circuit.

The relay is mounted in position with associated piping and isolating valves at works. In larger transformers, the buchholz relay assembly is dismantled and sent separately. When Test Lever is provided, it is sent in ‘Test’ position to prevent damage in transit. On receipt at site, check the relay for any damage to window glasses and mercury switches.

Mount the Buchholz relay between conservator and transformer tank cover along with piping & valves without straining the pipeline. Isolating valve must be fully opened after mounting is completed. To ensure successful operation of the relay the pipe work on either side of the relay is set inclined to horizontal by 3-5”.

MOUNT RELAY SUCH THAT ARROW DIRECTION POINTS TOWARDS CONSERVATOR

After filling oil in the transformer, air trapped inside the relay is to be released through the valve/petcock provided on top of buchholz collection, it must be ensured that this valve is kept open & the pipe is full of oil. When gas is collected, oil from pipe will flow out first and then gas will come out.

  - Radiators:

The function of radiators is to limit the temperature of oil and winding by dissipating heat that is generated due to losses within the transformer while in service. The number of sections per radiator and the number of radiators per transformer will depend upon the losses and permissible temperature rise.

Distribution transformers are normally provided with Radiators welded to tank. Owing to transport limitation and possible transit damages, power transformers are provided with detachable radiators with radiator valves. At the time of dispatch, these radiators are detached and sent separately keeping the valves in position on tank flanges.

  - Each radiator consists of number of ‘Sections made from pressed CRCA Sheets forming channels for oil flow. These ‘Sections’ are welded to header pipes at Top & Bottom. Detachable radiators are provided with M.S. Flanges at Top & Bottom. Flanged radiators are fitted with Air Release Plug, Drain Plug, Lifting Lug, ETC.

  - Bracing Straps, made from M.S. Flat are provided on radiators to prevent vibration of sections.

Radiators are cleaned internally to remove scales and a coat of varnish is applied. External surface is cleaned off all rust and one coat of Red Oxide primer is applied which is followed  by final painting.

  - Silica Gel Breather :

Whenever there is a change in the ambient temperature or in the load of an oil-immersed transformer, there is a change in oil temp. & hence in the volume of oil. Increase in oil volume, causes the air above the oil level in the conservator to be pushed out and decrease causes air to be drawn in. Thus the transformer ‘Breathes’. When air is breathed in, there is a possibility of moisture and dust from atmosphere to be sucked in. These contaminants deteriorate the insulation properties of oil. Hence, Silica Gel Breather is provided which arrests moisture and dust from the air drawn in.

A typical –Silica Gel Breather has following main components:

1) A Casing, 2) Silica Gel Crystals, 3) An oil seal at the lower end of casing.

The casing has a window at the upper part for observation of the color of the gel crystals. It has a flange connection at the top for connecting the breather to the breather pipe. The lower part of the casing has at its lower end an oil seal arrangement, a window for observation of oil level and an oil filling hole with gasket & plug.

Due to the chemical affinity possessed by Silica Gel Crystals, they absorb moisture from the air drawn in. The color of silica gel is blue when dry and turns pink when it is saturated with moisture. The color of crystals can be observed from outside of the casing.

Oil seal assembly at the lower end of the casing consists of a little quantity of oil with an inverted cup partly dipped in the oil and a tube fixed at the centre of the cup.

The oil acts as a coarse filter and removed the dust from the outside air when it passes through oil.

Silica gel breather is dispatched in a separate case.

  - Magnetic Oil level Gauge (MOG) :

This is a dial type oil level indicating device provided on large transformers with conservator at relatively high levels from the ground. In large transformers conventional glass oil level indicators are difficult to observe due to their heights and color change/dust accumulation on the glass. Further, the low oil contacts provided on the magnetic oil level indicator can be used for automatic alarm when the oil level in the conservator falls to a low level. This protection feature and clear visibility justify the cost of MOG on a bigger transformer.

It consists of two compartments :

- The oil side compartment which is fixed on the opening in the conservator.

- The pointer side compartment.

These compartments are sealed against leakage of oil by a metallic diaphragm. On the oil side compartment, there is a bevel gear wheel and it is positioned near the diaphragm. Movement of the float due to rise and fall of oil level in the conservator results into circular motion of the driving magnet. A follower magnet is positioned in the pointer side compartment near the diaphragm. This magnet has its poles face to face to the poles of driving magnet from the oil side compartment coupling them magnetically. The movement of float is, therefore, transferred through the diaphragm, eliminating direct oil light mechanical coupling.

At the other end of the axis of the driven magnet an indicating pointer is fitted. The dial is calibrated to show the oil leveling the conservator. The dial and the pointer area housed behind the front glass. The dial has three positions marked. The follower magnet has also a cam fitted on it which operates a mercury switch. When this magnet is at a position corresponding to low oil level the mercury switch closes the Normally open (NO) contacts. These contacts are normally wired to give audible alarm. The contacts are brought to a terminal box at the lower end of the dial, for external connections.

  - Oil Temperature Indicator (O.T.I.) :

  - Oil Temperature indicator (O.T.I.) is generally provided on all transformers except for very small ratings. The direct reading pointer arrangement in this Instrument greatly facilitates observation of working temp. of oil. It also helps, if need be, in deciding the permissible overloads in accordance with I.S.6600-1972. Guide for loading of oil immersed transformers.

  - A typical-Oil temperature indicator consists of a

  - Bourdon tube with a pointer arrangement mounted in a case comprising of a reading dial and a glass cover. There is a temperature sensing bulb which communicates to the Bourdon tube through the armoured capillary.

  - The oil temperature indicator is provided with two pointers and associated contacts for protection of transformers. Both the pointers are independently adjustable and can be set to desired temperature. Setting of these pointers at required temperatures can be done from outside through the knob by using special keys.

  - The OTI is generally housed and wired upto terminal strip in the marshalling box having a glass window on the door for observation. The length of capillary does not influence the accuracy of measurement and extra length of capillary tubing must not be cut, as it would break communication between bulb and Bourdon tube.

If the temperature increases beyond set limit due to overload or inadvertent closure of radiator valves or insufficient air draft, the indicating pointer touches the present alarm pointer and actuates the alarm contacts. The alarm contacts, when duly wired give an alarm. If the alarm is not attended and there is a further increase of temperature, the trip contacts which are wired to the trip circuit will operate and isolate the transformer from mains.

  - Winding Temperature Indicator (W.T.I.):

Generally for transformers of high power rating a winding Temperature Indicator is also required and provided.

A typical –Winding Temperature indicating (W.T.I.) arrangement provided in a transformer comprises of the following :

- W.T.I. Pot

- Image Coil

- W.T.I. C.T.

- W.T.I.

The W.T.I. Pot is mounted at the top of the transformer tank. Hence the oil in the W.T.I. Pot is at a temperature of TOP OIL. The image coil is a heater coil and develops additional heat raising the temperature of the oil inside the heater coil. There is a W.T.I. C.T. mounted on one of the line leads with its secondary feeding the image coil. As the load on the transformer varies, the line current varies, the W.T.I. C.T. secondary current passing through the Image Coil varies, the heat developed by Image coil varies and hence the temperature of the oil inside the Image coil varies. The bulb of the W.T.I. is immersed in the oil inside the Image Coil and as seen above the temperature of this oil is dependent on Top Oil Temperature and the Load on the transformer.

The W.T.I. Image coil is designed and calibrated to indicate the Winding Hot Spot Temperature (HST) because this is the temperature which decides the life of he transformer. Thus the winding Temperature indicator(W.T.I.) reads temperature.

= Ambient Air 	+             Top Oil 		+ 	1.1 X GRADIENT

Temperature		   Temp. Rise.

Winding Temperature Indicator is also housed in the marshalling box. W.T.I. also has an alarm and trip contacts which are wired upto terminal strip. For fan cooled transformers, the auxiliary contacts of W.T.I. are used for switching ON and OFF the fans.

3.		INSTALLATION & COMMISSIONING:

  - GENERAL :

This section illustrates procedure for Installation & Commissioning of our transformers.

A format of ‘Commissioning Report’ is included at the end of this section. Results of various precommissioning tests as well as confirmation of checkpoints are to be recorded in this Report. This Report then would serve as a handy record for future reference.

  - INSTALLATION:

    - Location :

The transformer should be kept in a well ventilated place, free from excessive dust, corrosive fumes etc. Adequate ventilation is necessary for tank and radiators so that they can dissipate heat. There should be clear space of about 1.25m on all sides of the transformers if it is enclosed in a room.

    - Foundation:

Foundation should be firm, horizontal and dry. Where rollers are fitted, suitable rails should be provided.

    - Provisions for Oil Draining:

Necessary provisions for oil draining, in the event of a fire, should be made by way of Oil Soak Pits. Fire Seperation walls should also be provided when necessary.

    - Assembly of Dismantled Components:

Various components dismantled for transportation should be duly assembled.

      - Main tank:

Keep the main tank in its permanent position of operation. Lock the rollers to prevent any accidental movement of rails. Draw an oil sample from the bottom of the tank and test it for Break-Down-Voltage (BDV).

Note this value in ‘Commissioning Report’

      - Bushing:

Clean the bushings and check that there are no hair-cracks or other damages. Test IR value of each bushing with a 500V Megger. It should be 100 M ohms or greater. Note details of Bushings in the ‘Commissioning Report’. Mount all the bushings as described in 2.6. Ensure that the test tap cap is fully tightened, thus positively grounding the same. Adjust the Arcing Horn Gaps in accordance with the Insulation Co-ordination Note these values in the ‘Commissioning Report’.

      - Conservator & M.O.G:

Note details of M.O.G. in the “Commissioning Report”. If the M.O.G. is provided with a locking lever, it should be removed. Mount the conservator. When there is an OLTC its conservator is some times provided separately or by making a partitioned compartment in the main conservator. OLTC conservator, if separate, should also be mounted.

      - Buchholz Relay:

Note details of “Buchholz Relay” for the transformer and of “Oil Surge Relay” for the OLTC in the “Commissioning Report”. Buchholz Relay floats are tied to prevent transit damage. They should be released. Also if ‘Test’ lever is provided, it should be in the working position. Mount the “Buchholz Relay” and the shut off valves as described in 2.6 Similarly mount “Oil Surge Relay”.

      - Breathers:

Note details of Breathers, in the “Commissioning Report”. If OLTC is provided, it may have its own separate breather. Note details of these Breathers also in the “Commissioning Report”. Check that the color of Silica Gel in Main Breather is Blue. Remove the rubber cap closing the breather opening. Similarly mount the OLTC breather.

      - Radiators:

Note the details of Radiators and Radiator Valves in the “Commissioning Report”. Mount the radiators as outlined below:

- Radiators are to be assembled only one at a time

- Oil required to fill in the radiators is sent separately in drums. Test oil sample from each drum for BDV. Ensure it is more than minimum specified in I.S. 1866 for New Transformer.

- Fill the conservator full using an oil filter machine, If available.

- Clean one radiator externally. Remove blanking plates and clean the gaskets and radiator flanges. If gaskets are damaged, use spare gaskets.

- If blanking plates are not in position and it is suspected that foreign material might have entered the radiators, clean them internally by flushing fresh and clean transformer oil.

- Oil might seep through the tank side radiator valves and be retained by the blanking plates. This should be collected in a clean container at the time of removing top and bottom blanking plates.

- Bring the radiator flanges close to the flanges on the tank. Ensure that tank gasket is in position. Fit by means of bolts, nuts, spring washers etc.

- Open the bottom radiator valve using the operating handle. Gradually unscrew the air release plug on the top of the radiator, until air starts escaping. Air Release plug should not be removed from the engaging threads as it would be difficult to control oil coming out of it. Oil from main tank will now flow in the radiator, driving out air form air release plug. When oil comes out steadily from the air release plug and no more air comes through, close the air release plug. Open the top radiator valve. Oil level I the conservator would now have fallen. Check that there is no oil leakage from the radiator itself and the gasketted joints. Restore the oil level and assemble the next radiatorin the same manner.

Assembly of radiators should be proceeded in only one direction-clockwise or anticlockwise. After filling last radiator, oil level in conservator should be restored only upto the filling mark.

When OLTC compartment is provided in the main conservator, this compartment is to be separately filled upto its filling mark.

      - Marshalling Box:

Marshalling box should be fitted in position. Pockets of O.T.I. & W.T.I. should be filled with transformer oil. Bulbs of O.T.I. & W.T.I. should be fitted in position in their respective pockets.

Set the ‘Alarm’ & ‘Trip’ contacts of O.T.I.& W.T.I. at required values. O.T.I. setting of A=850C & T=950C W.T.I. setting of A-950C & T-1050C are considered good.  They can be worked out to suit local conditions.

Note details of O.T.I. & W.T.I. and their settings in the “Commissioning Report”.

      - Cable Box:

When Cable boxes are provided they should be mounted and cable terminations done. Oil filled cable-boxes should be duly filled with oil. In case of “Bus-Duct” connections, transformer is provided with a flange to receive the bus-duct. Due connection and fitting should be done to over-head line by a terminal connector.

      - Other fittings:

Note the details of other important fittings like fans in the “Commissioning Report” and mount these fittings.

    - Oil Sampling & Filteration:

Taking usual precautions, draw oil samples from bottom & top of main tank and from OLTC. They should be tested for BDV. If they meet the requirements if I.S.1866 for new transformers, no further processing is required. However, if they do not meet the requirements oil needs to be filtered till the required BDV is obtained. Note the BDV values in the “Commissioning Report”.

    - Air Release:

Release air by slowly unscrewing Air Release Plugs provided at Bushings, Bushing Pockets, Buchholz Relay, Main Tank Cover, Oil Surge Relay etc. From plain porcelain bushing of 11,22 & 33KV, air can be released by loosening the nut pressing the rubber gasket and pressing the metal part down.

  - COMMISSIONING:

    - Pre-commissioning Test:

Prior to energizing the transformer, several pre-commissioning tests are done. The objective of these tests is to confirm that the transformer has not suffered damage during transit and also to check any inadvertent slips in the factory tests, or supply.

      - Ratio Test:

Ratio between all the three corresponding H.V. &L.V. phases is to be measured on all taps. It is desirable to do this test by a Ratio-meter. But if it is not available, a simple test of measuring voltages can also serve the purpose.

Referring to R&D plate, find out which terminals of H.V. & L.V. correspond to one phase e.g. for a vector Group of Dyn-11, H.V. Terminals 1U,1V & L.V. terminals 2U, 2N correspond to U Phase. Apply single phase, 415V or 240V, AC., 50Hz to H.V side and measure voltage on the L.V. side. Measure these voltages on all taps and note them in “Commissioning Report”. Repeat for the other two phases. These observations should indicate a consistent trend of variation in line with the details given in R &D Plates. Numerical values should approximately check with the voltage ratio.

      - Vector Group Check Test:

Connect terminals 1U, 2U together. Apply 3 phase, 415V, 50Hz. AC. to H.V.terminals 1U, 1V, 1W. Measure voltages between terminals 1V-2V,

1V-2W & 1W-2V, 1W-2W (or suitable other voltages if required). Check that the measured voltages confirm the relative position of H.V. & L.V. vector group. For vector group Dyn-11, the method is illustrated below.

1U,2U

2V

2W

2U

2V

2W

1W					 1V

H.V & L.V. vectors are shown independently positioned for Dyn-11, For the condition 1U & 2U connected together, L.V. Vectors are redrawn as shown. With this configuration, voltages 1V-2V& 1V-2W will be equal while 1W-2V will be greater than 1W-2W.

The method can be extended to any other Vector group. Note the observations in the “Commissioning Report”.

3.3.1.3		Magnetising Current Test:

Apply  415 volts, 2 Phase, AC. to the H.V.terminals, keeping the L.V. terminals open & tapping switch in the normal position. Measure the 3 line currents, if possible simultaneously, otherwise one after the other. Because the 3 phases of the magnetic circuit of the core are not similar, the 3 line currents will be approximately equal & v phase current around 80% of either of them. If  H.V. is delta connected, V & W phase currents will be approximately equal and U Phase current around 110%.

In case of power transformers, such a test is done, some times, along with routine tests at the manufacturer’s works. When done at site and results compared with the factory test confirms that there are no transit damages to the core & windings. Note the observations in the “Commissioning Report”.

3.3.1.4             Magnetic Balance Test:

This is a simple test to detect shorted turns in a winding. Its principle is that shorted turns oppose establishment of flux in that limb because of the current that circulates through the shorted turns.

As indicated in 3.3.1.2 Apply Single Phase, 415 or 240V, AC. to such H.V. line terminals which would energies U phase. (outer limb) Use an averaging instrument like a Multimeter.  Measure the voltage induced in the V phase (Centre limb) and W phase (other outer limb). Measure also the current drawn by the energized phase. In case the H.V. Voltage is 66Kvand above, the current drawn may be very small. In that case, L.V.would generally, be 11KV or more. This test can, then, be carried out on L.V. Side.  Centre limb being nearer to the energized limb, more flux passes through it and less flux in the outer limb. The division is around 70-30% & hence the measured voltages will be having approx this proportion. Next, energize W Phase and measure the other two voltages as before. Results should be similar to previous ones. Then energize V Phase (Centre limb). As both the outer limbs are symmetrically located w.r.t. centre limb, flux will divide equally between them. Hence the voltages measured on outer phases will be approx. equal. Also, for reasons explained earlier, currents drawn when outer phases are excited, will be equal that for centre phase will be less (approx. 70%). Thus these observations will confirm the healthiness of the windings.

In case one of the phases has shorted turns, it will draw a comparatively large current when it is energized. When other phases are energized, flux and hence voltage in the shorted phase will be significantly reduced. Hence all three observations will indicate the shorted phase. Note the observations in the “Commissioning Report”.

When the Magnetic Balance Test indicates a shorted phase, commissioning can not be undertaken. Contact us immediately giving detailed test results.

      - Measurement of Insulation Resistance:

Measure Insulation Resistance (IR) between windings and between windings and earth with a 2500/1000V Megger, preferably motor driven, otherwise hand-driven. Before measuring I.R., thoroughly clean all the bushings with clean cotton cloth, if required using Carbon Tetrachloride.  Also, there should be no external connections to the transformer terminals. Check and adjust, if required, the infinity setting of the Megger. Lead wires from the Megger to the transformer should run independently and be permanently clamped. They should not have any joints. It is known that the I.R. reading continues to increase initially and for comparison purpose, reading is to be taken at 1 minute of energizing. It is also known that I.R. value is dependent on temperature. Hence temperature at the time of measurement should be noted. Compare the I.R. values measured, with the factory results keeping in view the temperature at the time of measurement. Note the observation in “Commissioning Report”. Also measure and note the I.R. values of the Power Cables.

3.3.1.6		Short-Circuit Test:

For the H.V.side voltage and the % impedance, it would be possible to calculate the current which would flow in the H.V. side, with 415V applied to it, while keeping L.V. side shorted. If the 415V source can feed that current, a short-circuit test can be carried out.

This test would confirm proper contact engagement at all tap positions. Apply 3Ph. 415V, 50Hz to H.V side, keeping L.V. side shorted. Measure the 3 line currents at all tap positions. If the switch is an OFF-CIRCUIT switch, supply has to be disconnected before changing tap. Note the observations in the “Commissioning Report”. Note also details of OLTC, if any.

A consistent trend indicates healthiness. If short-circuit test is not possible due to limitation of source carry out one tap changing operation over the entire range increasing as well as decreasing. Check the other modes of OLTC operation and note in “Commissioning Report”.

      - Parallel Operation:

Sometimes, the transformer to be commissioned is required to run in parallel with an existing transformer. In this case, the following conditions must be fulfilled by the incoming transformer:

    - Its voltage ratio is same as the existing transformer on all tappings

    - Its % Impedance is within ± -1% pf value of existing transformer.

NOTE: Due to difference in % impedances, when one transformer reaches its rated load, the other would share less than its rated load. As a result, the combination can supply load less than the sum of the two KVAs.

3)    Rated KVAs of the two transformers to be connected in parallel

should not differ by more than 1:3 as otherwise only marginal

increase will be obtained in the capacity of the combination.

4)    Vector group is compatible. If the vector groups of the two are

such that terminals to be paralleled have a phase different then

they can not be connected in parallel. Hence only certain Vector

Groups are compatible with each other.

If possible, one should check zero voltage between the

corresponding phases to be paralleled.

3.3.2		Other Relevant Details:

Other controlling and protecting equipments like C.T.s, Breakers, relays etc.

form a part of the transformer installation. Note their details in

“Commissioning Report”.

3.3.3		Check Points:

After completing installation and precommissioning tests, check that the

various points mentioned in the “Commissioning Report” have been complied

with. Compliance notings should be made in the “Commissioning Report”

    - Energizing:

When all the pre-commissioning tests are found satisfactory and all the check points are confirmed the transformer can be energized on No load. It is preferable to keep settings of all protective relays to the minimum. The transformer should be allowed to run on No-load for about3 hours. During this period, the transformer should be observed for any abnormality in the hum and gas collection in the Buchholz relay. Sometimes during this period, trapped air is released and gets accumulated in Buchholz Relay.

At the end of this 3 hours period, transformer should be de-energized and air released from Bushings, energized again and the relays set at their desired settings. Transformer should then be gradually loaded reaching full load in about 3 hours time. During the period and for further 3 hours, (i.e. total of 6 hours) transformer should be under observation. Check that all instruments, O.T.I. & W.T.I., M.O.G. are reading properly and that all radiators are uniformly hot. Check that there is no gas collection in Buchholz relay. If everything is found in order, the transformer can continue working.

The “Commissioning Report” should be duly signed by the Authorised representatives of all the participating organizations.

    - Tools & Instruments Required For installation/ Maintenance of Transformers:

Tools:

The following tools are required at the time of installation of transformers.

a) 20mm φ or 12mm φ Vinyl hose to take oil samples from drums		1 No.

b) Drum Opener								1 No.

c) Crow bar, Pipe roll, Hammers etc. for package shifting & opening	As required

d) 25mm dia. Manila Rope							50 Meters

e) Chain Pulley Block-1 Ton capacity and lift about 10 meters		1 No.

f) Small size screw spanners-100mm long for nuts upto 6mm size		2 Nos.

g) Hand lamp for inside working						1 No.

h) Screw drive-200mm & 300mm long					1 No. each

i) Pipe Wrench-250mm size.							1 No.

j) Cutting Pliers (Insulated)							2 Nos.

k) PVC Wire for connecting Meters						As required

l) Spanners

M			24			1

M			20			2

M			16			2

M			12			2

M			10			2

M			8			2

The following instruments are required for testing:

- Oil testing kit to test the break-down voltage of Transformer oil.

- 2500 Volts megger to measure the Insulation Resistance (IR) values.

- Two Voltmeters, one of 0-100V range and another of 0-500V range, to read the L.T side and the applied voltage during voltage ratio test.

- One AVO Meter.

3.3.6		Commissioning Check Points:

1.   Oil Samples from main Tank & O.L.T.C.

have passed BDV requirement   					YES/NO

1a.  Bushing surfaces are cleaned.					YES/NO

2.   Test Tap Caps are fully tightened					YES/NO

3.   Arching  Horn-gaps are duly adjusted				YES/NO

4.   Oil level in main conservator is upto mark.			YES/NO

5.   Oil level in O.L.T.C. Conservator in separate			YES/NO

Conservator or compartment in main conservator

6.   M.O.G. lock is released.						YES/NO

7.   Buchholz relay lock is released.					YES/NO

8.   Buchholx Relay Test Lever is kept in ‘S’ Position		YES/NO

9.   Buchholz relay shut off valves on both sides are open.		YES/NO

10.  Air release valve of Buchholz Relay is closed.			YES/NO

11.  Buchholz relay arrow head is pointing towards conservator.	YES/NO

12.  Lock of Oil Surge Relay (OSR) on O.L.T.C. is released.	YES/NO

13.  OSR shut off valve is open.					YES/NO

14.  OSR arrow-head is pointing towards conservator.		YES/NO

15.  Color of Silica Gel in main breather is blue.			YES/NO

16.  Oil is filled in main Breather upto level mark			YES/NO

17. Sealing tape of main Breather is removed			YES/NO

18. Color of Silica Gel in O.L.T.C. breather is blue			YES/NO

19.  Oil is filled in O.L.T.C. breather upto level mark.		YES/NO

20.  Sealing tape of O.L.T.C. breather is removed.			YES/NO

21.  All radiator valves-Top and bottom are open.			YES/NO

22.  Valve connecting Main tank to cable Box is open.		YES/NO

23.  Oil is filled in Disconnecting Cable Box upto Level Mark.	YES/NO

24.  All sampling, drain and filtration Valves are closed.		YES/NO

25.  Oil filling cap on main conservator is duly filled.		YES/NO

26.  There is no oil leakage from any where.				YES/NO

27.  Explosion vent diaphragms are intact and there is no 		YES/NO

oil in explosion vent.

28.  Oil is filled in O.T.I./W.T.I.					YES/NO

29.   Air released from:

i) All Bushings							YES/NO

ii) All Bushings Pockets						YES/NO

iii) Buchholz Relay						YES/NO

iv) Main Tank Cover						YES/NO

v)  All radiators							YES/NO

vi) OSR on O.L.T.C.						YES/NO

vii) O.L.T.C. Tank Cover						YES/NO

30.  O.L.T.C./Off Circuit Tap Switch is in the desired		YES/NO

position and is properly locked.

31.  Tank earthing is done.						YES/NO

32.  Neutral earthing is duly done.					YES/NO

33.  Rollers are locked						YES/NO

34.  C.T. secondary terminals, if not wired,				YES/NO

are shorted & earthed.

35.  Alarm & Trip contacts of O.T.I. & W.T.I.			YES/NO

are set at the required values.

36.  External connections are dully tightened.			YES/NO

4.		OPERATION & MAINTENANCE:

4.1		OPERATION:

I.S.2026-1977 states that a Power Transformers loaded at its rated KVA will fulfill its

normal life when its hottest spot temperature (H.S.T.) is 980C for an air temperature of

320C . As the ambient air temperature exceeds 320C, the H.S.T. exceeds 980C. The

insulation ageing (which decides the life of transformer) increases with increase of

H.S.T. Increase of H.S.T. by 60C doubles the rate of ageing (i.e. reduces the life by

50%). When the ambient air temperature is lower than 320C, the H.S.T. is lower than

980C. The insulation ageing decreases thus increases the life of transformer.

It is considered (by the I.S. 6600-1972) that periods of accelerated ageing due to higher

ambient temperature are compensated by the periods of reduced ageing due to lower

ambient temperatures.

Sometimes a transformer may be required to deliver load higher than its rating.

Guidance on overloading is provided by I.S.6600 Basis for this recommendation is as

follows:

In a 24 hours loading, if ambient temperature is low and load for a substantial time

duration  is also low a short time over load may be permitted such that equivalent

ageing due to this varying load will be the same as that of loading over a period of

24 hours.

  - MAINTENANCE:

    - General:

Compared to most electrical equipments transformer requires relatively less maintenance. However in order to obtain a long and trouble free service from the transformer, it must be properly maintained. Maintenance consists of regular inspection, testing and reconditioning when necessary. Principal object of maintenance  is to maintain the insulation in good condition. Moisture, dirt and high temperature causes insulation deterioration i.e. ageing. Hence they must be prevented.

No work should be done on the transformer unless it is disconnected from all external circuits and all windings have been solidly earthed.

Naked lights and flames should be kept well away from the transformer.

Precautions must be taken to secure tools with tapes to prevent them from falling inside the tank.

Maintenance hints on main constituents of the transformer are given in the following paragraph.

Recommended frequency of maintenance is given at the end of the chapter. Detailed guidance on Maintenance is given in I.S.10028 (part III)-1981.

    - Oil:

In the transformer, oil is used as an insulating liquid as well as for cooling. It is necessary to maintain required oil level and also to maintain this oil in good condition

I.S. 1866 gives recommendations in details for the maintenance of oil. A few guide lines are given here.

- Check if there is any leakage of oil. If noticed, corrective actions must be immediately taken.

- The oil level should be checked at frequent intervals and if necessary, topping up should be done with oil complying with I.S.335.

- Samples of oil should be taken at regular intervals and tested.

- If the dielectric strength is below the value recommended in I.S.1866, the oil should be duly filtered. It may be noted that the products of decompositions viz. water, acids etc. remain in the oil and accelerate the rate of ageing. Thus, timely treatment of oil is a must. The filtration will remove moisture, dust, sludge etc. Removal of sludge is important as otherwise it can stick to coils and hamper the heat dissipation from coils. However, if the results indicate that acidity needs to be improved, then a simple filtration would not be sufficient and a Fullers Earth treatment would be required.

    - Core & Winding:

It is recommended that the core and windings are removed from the tank for visual inspection as per the maintenance schedule given. Depending upon the arrangement provided, tap switch handle, connections to bushings etc. may have to be disconnected before lifting up core and windings assembly.

The windings should be examined and if sludge has been deposited it should be washed away with oil jet. Any loose nut and bolt should be tightened.

Adjust tie rods/coil clamping screws provided to remove any slackness of windings. This is important as slackness in windings will permit movement of coils under the action of Short Circuit force and repeated coil movement can wear out insulation and give rise to a fault.

    - On Load Tap Changer:

On load tap changer is, normally, mounted on the tank in the separate housing and connected to winding leads through copper studs fixed on an insulated terminal board.  Terminal board is oil-tight. Hence oil in the tank need not be lowered for attending O.L.T.C.

In some other types, O.L.T.C. is housed in the main tank by suitable mounting on the top cover. Here again O.L.T.C. oil in which arcing takes place is not allowed to mix with the main tank oil.

Please refer to O.L.T.C. manual for operation and maintenance instructions of O.L.T.C.

    - Conservator and Oil level Indicator:

The inside of conservator should be cleaned by flushing, clean transformer oil to remove sludge and other impurities. In bigger transformers, detachable end plate is provided to facilitate cleaning of conservator.

  - Oil gauge glass should be cleaned. If the glass is found broken, the same should be replaced.

  - Magnetic oil gauge is also to be attended while cleaning the conservator. The mechanism should be inspected and cleaned. Float should be checked to see that there is no oil in the float. The operation of alarm and trip contacts should to be checked.

    - Silica Gel Dehydrating breather:

Breather should be examined to ascertain if the silica gel requires changing. More frequent inspections are needed when the climate is humid and when transformer is subjected to fluctuating load. The color of Silica Gel crystals in the breather acts as an indicator as it changes from blue to pink when saturated with moisture. When majority of crystals have turned pink, the silica gel should be reactivated by heating in oven or a shallow pan at a temperature of 1500C to 2000C until the original color is gained. This usually takes 2 to 3 hours. Oil cup should be cleaned to remove dust and dirty oil. Oil seal should be filled with fresh oil.

    - Buchholz Relay:

Routine operation and mechanical inspection should be carried out as per the manufacturer’s instructions.

    - Pipe Work:

The pipe work should be inspected for leakages, which may be due to bad seated joints. Joints should be re-made, and leakage stopped.

    - Explosion Vent:

The diaphragm at the exposed end of the explosion vent should be inspected and replaced if damaged. Failure to replace the diaphragm quickly may allow the ingress of moisture in the transformer.

Whenever bottom diaphragm ruptures, oil rises inside the explosion vent pipe and is visible in the oil level indicator on explosion vent. If diaphragm is broken because of fault in the transformer, inspection should be carried out to determine the nature and cause of the fault.

    - Gaskets:

Gaskets sometimes shrink during service. It is, therefore, necessary to check the tightness of all bolts/fasteners of gasketted joints. The bolts should be tightened evenly around the joints to avoid uneven pressure. Leaky gaskets should be replaced as soon as the circumstances permit.

    - Temperature Indicators:

The capillary tubing should be fastened down again if it has become loose. Dial glass should be kept clean. It should be replaced if damaged, to prevent damage to the pointer. Temperature indicators found reading incorrectly should be calibrated with standard thermometer using hot water bat. Check the pocket/s for presence of water and if found, clean the pocket and refill with fresh oil and seal the opening properly. If Armour of capillary is exposed, then retaping must be done by PVC tapes.

    - Bushing:

Porcelain insulators should be cleaned and minutely examined for any cracks, chipping off & other defects. All such bushings should be replaced. In case of any sign ofoil leakage from the condenser bushings the matter should be referred to us.

    - External connections Including Earthing:

Check all external electrical connections including earthing. They should be tight. If they appear blackened or corroded, unbolt the connection and clean with emery paper.

Remake the connections and give a heavy coating of conducting grease. It is particularly important that heavy current carrying connections are properly made as any loose connections give rise to heat generation & temperature rise which could be detrimental to the connection.

MAINTENANCE SCHEDULE

FOR DISTRIBUTION TRANSFORMER

Recommended frequency of maintenance is given below. Detailed guidance on Maintenance is given in I.S. 10028 (part II)- 1981.

| Sr. No. | Inspection Frequency | Items To Be Inspected | Inspection Notes | Action Required If Inspection Shows Unsatisfactory Condition | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1. | Hourly | (i) Ambient Temperature (ii) Winding Temperature (iii) Oil Temperature (iv) Load(amp) (v) Voltage | - Check that the temperature rise is reasonable. Check against rated figure. | - Shut down the transformer and investigate if either is persistently higher than normal. Control load. Adjust tap. |  |
| 2. | Daily | (i) Oil level in Transformer on load tap changer (ii) Explosion vent (iii) Dehydrating breather | Check against Transformer oil temperature. - Check colour of the active agent and that opening is not clogged. | If low, top up with dry oil, examine transformer for leaks. Replace if cracked or broken. If silica gel is pink change by spare charge. The old charge may be reactivated for further use. |  |
| 3. | Quarterly | (i) Bushing (ii)Oil in transformer and tap changer. (iii) Cooler fan and pump bearings and motors & operating mechanism. (iv) On load tap changer-driving mechanism. (v) On load tap changer automatic control. (vi) Dehydrating Breather. (vii) Ventilators (in case of indoor transformers) | Examine for cracks and dirt deposits. Check for dielectric strength and water content. Lubricate bearings, check gearbox. Examine contacts. Check manual control and interlocks. Check oil. Check all circuits independently. Check step-by-step operation including limit switches. Check oil level in oil cup. Check that air passages are free. | Clean or replace as necessary. Take suitable action to restore quality of oil. Replace burnt or worn out contacts or other parts. - - Make up oil if required. - |  |
| 4. | Yearly(or earlier if transformer can conven-iently be taken out for checking) | (i) Oil in transformer and sludge. | Check the acidity | Filter or replace. |  |
|  |  | (ii) insulation resistance | Compare with values at the time of commissioning. | Process if required. |  |
|  |  | (iii) Gasketted joints. | - | Tighten the bolts evenly to avoid uneven pressure. |  |
|  |  | (iv) Cable boxes. | Check for sealing arrangements for filling holes. Examine compound for cracks. Check moisture condensate if any in air filled boxes | Replace gaskets, if leaking. |  |
|  |  | (v) Relay alarms, their circuits, etc. | Examine relay and alarm contacts and their operation, fuses, etc.Check relay accuracy, etc. | Clean the components or replace contacts and fuses, if necessary. change the settings if necessary. |  |
|  |  | (vi) temperature indicator | Pockets holding thermometers should be checked. | oil to be replenished, if required. |  |
|  |  | (vii)Dial type oil gauge | Check pointer for freedom of movement. | Adjust if required. |  |
|  |  | (viii) Paint work | Should be inspected. | Any painting or retouching should be done if necessary. |  |
|  |  | (ix) Earth resistance | - | Take suitable action if earth resistance is high. |  |
|  |  | (x) Surge diverter and gap | Examine for cracks and dirt deposits. | Clean or replace. |  |
| 5. | Two years | (xi) Non-conservator transformers | Internal inspection above care. | Filter oil regardless of condition. |  |
|  | -do- | (xii) oil conservator | Internal inspection | Should be thoroughly cleaned |  |
|  | -do- | (xiii) Buchholz relay | Mechanical inspection | Adjust floats, switches etc. as required. |  |
| 6. | 5 years | (xiv) transformers upto 3 MVA | Overall inspection including lifting of core and coils | Wash by hosing down with clean dry oil. Tighten coil Clamping arrangements and other bolts, nuts, if loose. |  |
| 7. | 7 to 10 years | (xv) transformers above 3MVA | -do- | -do- |  |